Chiller History:  11/2016 - last operational check within normal limits. 1/13/2017 - found unit nonfunctional; unit full of air and excessive oil in evaporative barrel.  From 6/2017 to 10/11/2017, repairs were made and placed back into service following assessment to reseal unit and replace pressure regulator, clean oil sump performed.  Unit appeared to function properly from 10/2017 to 9/2018.   From 5/2018 to July, 2018, several leak checks and pressure valve adjustments were performed.  Unit placed back into service. Functioning well until 1/2019.  Unit failed; full of air; deemed necessary to replace seal and rebuild compressor due to thrust tolerances exceeded.  Also, replaced bad IO board.  8/2019 - JCI rebuilt compressor, placed back into service.  Ran continuously for 960 hrs until time that it was shutting down for satisfied demand or extended periods of time, resulting in oil, once again draining sump into evaporator.  This occurred on 10/30/2019.  Cost spent on repairs to date approx. $88,000.00.